## Monthly

## INSPECTION / TESTING OF WATER STORAGE TANK

The State Fire Code requires you to inspect, test, and maintain fire protection systems in an operative condition. All inspection, testing and maintenance records are required to be kept on file at the premises.  Any questions concerning regulatory requirements for fire protection systems should be directed to your municipal code enforcement authority.  W & M Sprinkler will notify you in writing of any condition or deficiency discovered requiring correction or repair.  Any authorized repair/maintenance work will be performed either as quoted or on a time and material basis.

#### SCOPE OF WORK

- (Annually) Visually inspect expansion joints, where provided, for leaks and cracks.

- (Annually) Visually inspect hoops and grillage of wooden tanks.

- (Annually) Visually inspect exterior painted, coated, or insulated surfaces of the tank and supporting structure, where provided, for signs of degradation.

- (Annually) Test high and low water level signals.

- (Quarterly) Inspect heating system with supervised low water temperature alarm (if equipped).

- (Quarterly) Visually inspect the exterior of the tank, supporting structure, vents, foundation, and catwalks or ladders, where provided, for signs of obvious damage or weakening.

- (Quarterly) Visually inspect the area surrounding the tank and supporting structure to ensure the area is free of fire hazards, free of accumulation of material near parts that could result in accelerated corrosion or rot, free of ice buildup, and that the exterior sides and top of embankments supporting coated fabric tanks are free of erosion.

- (Quarterly) Inspect the water level if tank is equipped with supervised water level alarms.

- (Monthly) Inspect and record water temperature (during cold season only).

- (Monthly) Inspect the water level if tank is not equipped with supervised water level alarms.

- (Monthly) Inspect heating system not equipped with supervised low water temperature alarm.

- (Monthly) Test low water temperature signals, where provided, prior to the heating season.

- (Monthly) Test high water temperature limit switches on tank heat systems, where provided, prior to the heating season.

Excluded Work:

- Visual inspection of systems or portions of in inaccessible spaces.

- Any and all NFPA, State, and local requirements in excess of above stated.

Licensed by the NYS Dept of State – UID# 12000244389, UID#12000281635, UID#12000259060

Rev. 07-28-10