50 Broadway                       1433 Bassett Ave.              630-1 Broadway Ave.

Hawthorne, NY 10532        Bronx, NY 10461               Holbrook, NY 11741

Phone: 914-741-2222        Phone: 718-409-5616        Phone: 631-472-4500

- SEMI-ANNUAL INSPECTION & TESTING OF DRY CHEMICAL FIRE SUPPRESSION SYSTEM

The State Fire Code requires you to inspect, test, and maintain dry chemical fire suppression systems in an operative condition. All inspection, testing and maintenance records are required to be kept on file at the premises.  Any questions concerning regulatory requirements for fire protection systems should be directed to your municipal code enforcement authority.  W&M will notify you in writing of any condition or deficiency discovered in the annual inspection that will require correction or repair.  Any authorized repair/maintenance work will be performed either as quoted or on a time and material basis.

- (Semi-Annually) Attempt to visually inspect all known portions of system for exterior condition of nozzles, piping, and hangers from floor level only.

- (Semi-Annually) Test remote pulls and manual release of system.

- (Semi-Annually) Replace fixed temperature-sensing elements of fusible metal alloy-type.

- (Semi-Annually) Visually inspect suppression agent cylinder.

- (Semi-Annually) Check gauge for correct cylinder pressure (if applicable).

- (Semi-Annually) Identify last hydrostatic test date of agent cylinder if legible.

- (Semi-Annually) Inspect nozzles and verify that they are properly aimed, free of blockage, and have proper blow caps installed.

- (Semi-Annually) Visually inspect agent hoses.

- (Semi-Annually) Verify receipt of alarm, trouble, and supervisory signals at building fire alarm control unit and supervising station (if applicable).

- (Semi-Annually) Install record tag and compile report of inspection.

- (Annually) Operationally check pressure regulators.

Excluded Work:

- Agent discharge test

- Refill or add agent to storage container

- Flushing of system piping

- Hydrostatic testing of agent or discharge cylinders

- Repair or replacement of deficient parts.

- Any and all NFPA, State, and local requirements in excess of above stated.