50 Broadway                       1433 Bassett Ave.              630-1 Broadway Ave.

Hawthorne, NY 10532        Bronx, NY 10461               Holbrook, NY 11741

Phone: 914-741-2222        Phone: 718-409-5616        Phone: 631-472-4500

- SEMI-ANNUAL

- INSPECTION/TESTING OF KITCHEN HOOD FIRE SUPPRESSION SYSTEM

The State Fire Code requires you to inspect, test, and maintain kitchen hood fire suppression system in an operative condition. All inspection, testing and maintenance records are required to be kept on file at the premises.  Any questions concerning regulatory requirements for fire protection systems should be directed to your municipal code enforcement authority.  W&M will notify you in writing of any condition or deficiency discovered in the annual inspection that will require correction or repair.  Any authorized repair/maintenance work will be performed either as quoted or on a time and material basis. Owner is required to inform Company of any cooking equipment changes or modifications from original installation prior to every inspection.

- SCOPE OF WORK

- (Semi-Annually) Attempt to visually inspect all known portions of system for exterior condition of nozzles, piping, and hangers from floor level only.

- (Semi-Annually) Test remote pulls and manual release of system.

- (Semi-Annually) Perform automatic trip test & verify mechanical operation of system.

- (Semi-Annually) Replace fusible links when required

- (Semi-Annually) Restore & reset system to normal operation and install new break rod tamper device.

- (Semi-Annually) Visually inspect suppression agent cylinder.

- (Semi-Annually) Check gauge for correct cylinder pressure (if applicable).

- (Semi-Annually) Identify last hydrostatic test date of agent cylinder if legible.

- (Semi-Annually) Inspect nozzles and verify that they are properly aimed, free of blockage, and have proper blow caps installed.

- (Semi-Annually) Verify that proper fire extinguisher is available on-site.

- (Semi-Annually) Visually inspect agent hoses.

- (Semi-Annually) Verify receipt of alarm, trouble, and supervisory signals at building fire alarm control unit and supervising station (if applicable).

- (Semi-Annually) Verify gas/electrical shutoff.

- (Semi-Annually) Install record tag and compile report of inspection.

Excluded Work:

- Agent discharge test

- Refill or add agent to storage container

- Flushing of system piping

- Hydrostatic testing of agent or discharge cylinders

- Repair or replacement of deficient parts.

- Physical inspection of the hood and related ductwork

- Any and all NFPA, State, and local requirements in excess of above stated.